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Photograph 1. Office 214 indoor unit on 14 August 2027 after installation and before final room turnover.
	RECORD
	FINDING
	DATE AND SOURCE

	Installation
	Wall unit, line-set cover, circuit, disconnect, condensate, and seals present
	14 Aug | CES field photo

	Functional test
	Heating, cooling, controls, defrost, and condensate checks passed
	15 Aug | startup sheet

	Government use
	Unit placed in service and used for Office 214 environmental control
	Since 16 Aug | facility log

	Technical inspection
	Installed work is acceptable and may remain in place
	18 Aug | CES Mechanical Systems


Record conclusion The Government received and continues to use a technically acceptable system. This record establishes benefit and condition; it does not decide authority, liability, price reasonableness, or ratification.
/s/ HAL EMMERICH
Hal Emmerich
Mechanical Engineer, 713 CES
18 August 2027
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