EXERCISE USE ONLY
DEPARTMENT OF THE AIR FORCE
SHADOW MOSES AIR FIELD, ALASKA
AWARDED DESIGN EXTRACT
Task Order FA-27-005 | Campbell Hall Office 214
	Drawing
	M-214 Level 2 Mechanical Plan Office 214

	Issued
	14 February 2027 for construction

	Task-order value
	$26.40 million firm fixed price

	Design basis
	Office 214 served by AHU-2 and terminal unit VAV-2-14


[image: ]
The awarded mechanical plan shows two central-system supply diffusers and one return grille serving Office 214 through VAV-2-14. It does not show a wall-mounted indoor unit, outdoor condensing unit, dedicated refrigerant lines, condensate route, disconnect, or separate electrical circuit.


SCOPE AND EQUIPMENT CROSS CHECK
Awarded records for Office 214
Awarded task-order scope
CLIN 0001 includes phased Campbell Hall renovation, central air-handling and terminal-unit renewal, duct distribution, controls, electrical distribution, interior finishes, and commissioning. Office 214 is an administrative office served by AHU-2 and VAV-2-14. Added permanent equipment must appear in the issued design, equipment schedule, specifications, or an authorized written modification.
	RECORD
	AWARDED CONTENT
	CROSS CHECK

	M-214
	AHU-2 and VAV-2-14 distribution
	No dedicated split system

	M-601
	Mechanical equipment schedule
	No Office 214 split-system equipment

	E-214
	Level 2 power plan
	No dedicated circuit or outdoor-unit feed

	23 81 26
	Split-system specification where scheduled
	Office 214 is not scheduled

	Modifications 0001-0004
	Abatement, phasing, and unrelated changes
	No Office 214 mini-split addition


Scope conclusion The installed unit invoiced in IB-01 was outside the awarded work. No Contracting Officer modification added it before performance.
/s/ EMMA EMMERICH
Emma Emmerich
Major, USAF | Contracting Officer, 713 CONS
18 August 2027
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